## Slide 1: Topology - Abbreviations
BC = Backbone coupler
LC = Line coupler
DVC = Bus device
LR = Line repeater
PS/Ch = Power supply with choke
S = Brightness sensor
RC = Routing counter

## Slide 2: Topology – Overal view

## Slide 3: Line

## Slide 4: Area

## Slide 5: Several areas

## Slide 6: Individual address

## Slide 7: Coupler – gate function

## Slide 8: Coupler: Block diagram

## Slide 9: Coupler: Fields of application
Individual address
The coupler is used
als
> 0
> 0
> 0
= 0
> 0
> 0
= 0
> 0
Backbone line / Main line
Main line / Secondary line
Line extension
Backbone coupler
Line repeater
Line coupler
for
as
= 0
B
B
B
B
B
B
B
B
A
A
A
A
L
L
L
L
AREA
LINE
BUS DEVICE

## Slide 10: Coupler: Connecting several lines

## Slide 11: Example: group addressing
L11
L12
L13
L21
L22
L23
P1
P2
P = Push button L = Lights
S = Brightness sensor
S1
L23
0/2/11
0/2/11
5/2/66
5/2/66
P1
P2
S1
L11
L12
L13
L21
L22
Actuator
Sensors
5/2/66
5/2/67
5/2/67
5/2/67
Group addresses
Main groups:
0 = central functions
5 = e.g. floor 5
Middle groups:
2 = Lighting

## Slide 12: Internal line telegram

## Slide 13: Line-crossing telegram

## Slide 14: Area-crossing telegram

## Slide 15: Coupler: Routing counter

## Slide 16: Internal and external interfaces

## Slide 17: Example: Division of lines in a medium-sized project
Area |  | Line | 
No. | Comment | No. | Comment
0 | Area 0 | 0 | Backbone line
1 | West wing | 0 | Main line West
 |  | 1 | 1st floor
 |  | 2 | 2nd floor
 |  | 3 | 3rd floor
 |  | 4 | 4th floor
 |  | 5 | 5th floor
2 | East wing | 0 | Main line East
 |  | 1 | 1st floor
 |  | 2 | 2nd floor
 |  | 3 | 3rd floor
 |  | 4 | 4th floor
 |  | 5 | 5th floor

## Slide 18: Backbone / Line coupler classical structure

## Slide 19: Connecting lines via the LAN network
19

## Slide 20: Line coupler replaced by IP Router

## Slide 21: Old line coupler type